# The Interlocking of DC yard Switches

Interlocking of all HVDC transmission switchgear is implemented through DC station control software. These interlocking conditions work in both manual mode and automatic mode of the DC configuration control mode.

Remarks

The representation method of interlocking is illustrated with WN-Q15 as an example:

Interlocking logic

WN-Q15 opening position: WN-Q15

WN-Q15 closing position: WN-Q15

∧...stands for AND logic

∨...stands for OR logic

## Lahore Converter Station

| =WN-Q11 ON | =WN-Q21 =WN-Q1 >15s |
| --- | --- |
| =WN-Q11 OFF | =WN-Q1 |
| =WN-Q12 ON | =WN-Q21 =WN-Q24 =S1-WN-Q2 [(=P1-WP-Q11 = P1.WN-Q11 =P1. WN-Q12) (=P2-WP-Q11 = P2.WN-Q11 = P2.WN-Q12)] |
| =WN-Q12 OFF | =S1-WN-Q2 |
| =WN-Q13 ON | =WN-Q22 =WN-Q23 (=P1.WN-Q12 = P2.WN-Q12=WN-Q11 =WN-Q1 Idel <1.6%) |
| =WN-Q13 OFF | = P1.WN-Q12 = P2.WN-Q12 =WN-Q11 =WN-Q1 Idel <1.6% |
| =WN-Q21 | =WN-Q11 =WN-Q12 = P1.WN-Q11 =P2. WN-Q11 |
| =WN-Q24 | =WN-Q12 =P1-WP-Q12 =P2-WP-Q12 |
| =WN-Q22 | =WN-Q13 =P1.WN-Q12 =P2.WN-Q12 |
| =WN-Q23 | =WN-Q13 |
| =WN-Q1 ON | 1 |
| =WN-Q1 OFF | {=WN-Q11 (=P1-WP-Q11 =P1.WN-Q11 =P1.WN-Q12 =P2-WP-Q11 =P2.WN-Q11 =P2.WN-Q12) =WN-Q13[ P1 NBSF ACTIVE P2 NBSF ACTIVE =P1.WN-Q12 (=WN-Q12 =P2-WP-Q12) =P2.WN-Q12 (=WN-Q12 =P1-WP-Q12)] (=P1.WN-Q11 =WN-Q12 =P2-WP-Q12 =P2.WN-Q11 =WN-Q12 =P1-WP-Q12)} Idgnd <102.4% |
| = P1.WN-Q11 ON | =P1-WN-Q21 =P1.WN-Q22 =P1-WP-Q21 =WN-Q21(=S1-WN-Q2 =WN-Q1 =P1-WN-Q1) |
| =P1.WN-Q11 OFF | =P1-WN-Q1 |
| =P1.WN-Q12 ON | =P1-WN-Q1 =P1-WN-Q21 =P1.WN-Q22 =P1-WP-Q21 =WN-Q22 |
| =P1.WN-Q12 OFF | =P1-WN-Q1 =WN-Q13 |
| =P1-WN-Q21 | =P1-WP-Q11 =P1.WN-Q11 =P1.WN-Q12 = P1.Z1.Z11-Q12 = P1.Z1.Z12-Q12 |
| =P1.WN-Q22 | =P1-WP-Q11 =P1.WN-Q11 =P1.WN-Q12 = P1.Z1.Z11-Q12 = P1.Z1.Z12-Q12 |
| =P1-WN-Q1 ON | 1 |
| =P1-WN-Q1 OFF | (P1BLK P1ESOF) P1Idne <83% P1Udl ≤3% |
| =P2.WN-Q11 ON | =P2-WN-Q21 =P2.WN-Q22 =P2-WP-Q21 =WN-Q21 (=S1-WN-Q2 =WN-Q1 =P2-WN-Q1) |
| =P2.WN-Q11 OFF | =P2-WN-Q1 |
| =P2.WN-Q12 ON | =P2-WN-Q1 =P2-WN-Q21 =P2.WN-Q22 =P2-WP-Q21 =WN-Q22 |
| =P2.WN-Q12 OFF | =P2-WN-Q1 =WN-Q13 |
| =P2-WN-Q21 | =P2-WP-Q11 =P2. WN-Q11 =P2.WN-Q12 = P2.Z1.Z11-Q12 =P2.Z1.Z12-Q12 |
| =P2.WN-Q22 | =P2-WP-Q11 =P2.WN-Q11 =P2.WN-Q12 = P2.Z1.Z11-Q12 = P2.Z1.Z12-Q12 |
| =P2-WN-Q1 ON | 1 |
| =P2-WN-Q1 OFF | (P2BLK P2ESOF) P2Idne <102.4% P2Udl ≤3% |
| =P1-WP-Q11 ON | =P1-WP-Q21 =P1-WP-Q22 =P1-WP-Q12 = P1-WN-Q1 [=P1.WN-Q11 =WN-Q11 =WN-Q1 =WN-Q13 =P1.WN-Q12 (=WN-Q12 =P2-WP-Q12) =P1.WN-Q11 =WN-Q12 =P2-WP-Q12 =WN-Q13] =S1-P1-WP-Q22 S1-P1 OLT OFF |
| =P1-WP-Q11 OFF | P1BLK P1Idl ≤2% |
| =P1-WP-Q12 ON | =P1-WP-Q22 =P1-WP-Q11 =P1.WN-Q11 =P1.WN-Q12 =WN-Q24 =P2-WP-Q12 =S1-P2-WP-Q12 =S1-P1-WP-Q22 =S1-P1-WP-Q11 =S1-P1. WN-Q12 =S1-P1.WN-Q11 |
| =P1-WP-Q12 OFF | =P1-WP-Q11 =P1.WN-Q11 =P1.WN-Q12 Idme <1.6% |
| =P1-WP-Q21 | =P1-WP-Q11 =P1.WN-Q11 =P1.WN-Q12 =P1.Z1.Z11-Q11 =P1.Z1.Z12-Q11 |
| =P1-WP-Q22 | =P1-WP-Q11 =P1-WP-Q12 =S1-P1-WP-Q11 =S1-P1-WP-Q12 |
| =P2-WP-Q11 ON | =P2-WP-Q21 =P2-WP-Q22 =P2-WP-Q12 = P2-WN-Q1 [=P2.WN-Q11 =WN-Q11 =WN-Q1 =WN-Q13 =P2.WN-Q12 (=WN-Q12 =P1-WP-Q12) =P2. WN-Q11 =WN-Q12 =P1-WP-Q12 =WN-Q13] =S1-P2-WP-Q22 S1-P2 OLT OFF |
| =P2-WP-Q11 OFF | P2BLK P2Idl ≤2% |
| =P2-WP-Q12 ON | =P2-WP-Q22 =P2-WP-Q11 =P2.WN-Q11 =P2.WN-Q12 =WN-Q24 =P1-WP-Q12 =S1-P1-WP-Q12 =S1-P2-WP-Q22 =S1-P2-WP-Q11 =S1- P2WN-Q12 =S1- P2.WN-Q11 |
| =P2-WP-Q12 OFF | =P2-WP-Q11 =P2.WN-Q11 =P2.WN-Q12 Idme <1.6% |
| =P2-WP-Q21 | =P2-WP-Q11 =P2.WN-Q11 =P2.WN-Q12 =P2.Z1.Z11-Q11 =P2.Z1.Z12-Q11 |
| =P2-WP-Q22 | =P2-WP-Q11 =P2-WP-Q12 =S1-P2-WP-Q11 =S1-P2-WP-Q12 |

| 极1直流滤波器1 |  |
| --- | --- |
| =P1-Z11-Q11 | =P1-Z11-Q12 =P1-Z11-Q21 =P1-Z11-Q22 =P1-WP-Q21 DCF1 disconnector switch open inhibit |
| =P1-Z11-Q12 | =P1-Z11-Q11 =P1-Z11-Q21 =P1-Z11-Q22 =P1-WN-Q21 =P1-WN-Q22 |
| =P1-Z11-Q21 | (=P1-Z11-Q22>600S P1-Z11-Q11 =P1-Z11-Q12 =P1-Z11-Q21) (=P1-Z11-Q11 =P1-Z11-Q12 =P1-Z11-Q21) |
| =P1-Z11-Q22 | =P1-Z11-Q21 =P1-Z11-Q11 =P1-Z11-Q12 |
| 极1直流滤波器2 |  |
| =P1-Z12-Q11 | =P1-Z12-Q12 =P1-Z12-Q21 =P1-Z12-Q22 =P1-WP-Q21 DCF2 disconnector switch open inhibit |
| =P1-Z12-Q12 | =P1-Z12-Q11 =P1-Z12-Q21 =P1-Z12-Q22 =P1-WN-Q21 =P1-WN-Q22 |
| =P1-Z12-Q21 | (=P1-Z12-Q22>600S P1-Z12-Q11 =P1-Z12-Q12 =P1-Z12-Q21) (=P1-Z12-Q11 =P1-Z12-Q12 =P1-Z12-Q21) |
| =P1-Z12-Q22 | =P1-Z12-Q21 =P1-Z12-Q11 =P1-Z12-Q12 |
| 极2直流滤波器1 |  |
| =P2-Z11-Q11 | =P2-Z11-Q12 =P2-Z11-Q21 =P2-Z11-Q22 =P2-WP-Q21 DCF1 disconnector switch open inhibit |
| =P2-Z11-Q12 | =P2-Z11-Q11 =P2-Z11-Q21 =P2-Z11-Q22 =P2-WN-Q21 =P2-WN-Q22 |
| =P2-Z11-Q21 | (=P2-Z11-Q22>600S P2-Z11-Q11 =P2-Z11-Q12 =P2-Z11-Q21) (=P2-Z11-Q11 =P2-Z11-Q12 =P2-Z11-Q21) |
| =P2-Z11-Q22 | =P2-Z11-Q21 =P2-Z11-Q11 =P2-Z11-Q12 |
| 极2直流滤波器2 |  |
| =P2-Z12-Q11 | =P2-Z12-Q12 =P2-Z12-Q21 =P2-Z12-Q22 =P2-WP-Q21 DCF2 disconnector switch open inhibit |
| =P2-Z12-Q12 | =P2-Z12-Q11 =P2-Z12-Q21 =P2-Z12-Q22 =P2-WN-Q21 =P2-WN-Q22 |
| =P2-Z12-Q21 | (=P2-Z12-Q22>600S P2-Z12-Q11 =P2-Z12-Q12 =P2-Z12-Q21) (=P2-Z12-Q11 =P2-Z12-Q12 =P2-Z12-Q21) |
| =P2-Z12-Q22 | =P2-Z12-Q21 =P2-Z12-Q11 =P2-Z12-Q12 |
| 直流滤波器通用 |  |
| 高压侧隔刀-Q11 | Q12合 Q21分 Q22分 极母线Q21分 DCF1 disconnector switch open inhibit |
| 低压侧隔刀-Q12 | Q11分 Q21分Q22分 中线母线Q21分中性母线Q22分 |
| 高压侧地刀-Q21 | [(Q22合>600S Q21分) Q21合] (Q11分 Q12分) |
| 低压侧地刀-Q22 | 分 Q11分 Q12分 |

| 极1阀厅 |  |
| --- | --- |
| ACY P1-U-Q22OFF | main door close VHkey Lock ACY_CLD 无监视故障 |
| ACY P1-U-Q22ON | TRC_Disconnect open ACY_OPD 无监视故障 |
| ACD P1-U-Q21OFF | main door close VHkey Lock ACD_CLD 无监视故障 |
| ACD P1-U-Q21ON | TRC_Disconnect open ACD_OPD 无监视故障 |
| DCL P1-U-Q24OFF | main door close VHkey Lock DCL_CLD 无监视故障 |
| DCL P1-U-Q24ON | TRC_Disconnect open DLC_OPD 无监视故障 |
| DCH P1-U-Q23OFF | main door close VHkey Lock DCH_CLD 无监视故障 |
| DCH P1-U-Q23ON | TRC_Disconnect open DCH_OPD 无监视故障 |
| 极2阀厅 |  |
| ACY P2-U-Q22OFF | main door close VHkey Lock ACY_CLD 无监视故障 |
| ACY P1-U-Q22ON | TRC_Disconnect open ACY_OPD 无监视故障 |
| ACD P2-U-Q21OFF | main door close VHkey Lock ACD_CLD 无监视故障 |
| ACD P2-U-Q21ON | TRC_Disconnect open ACD_OPD 无监视故障 |
| DCL P2-U-Q24OFF | main door close VHkey Lock DCL_CLD 无监视故障 |
| DCL P2-U-Q24ON | TRC_Disconnect open DLC_OPD 无监视故障 |
| DCH P2-U-Q23OFF | main door close VHkey Lock DCH_CLD 无监视故障 |
| DCH P2-U-Q23ON | TRC_Disconnect open DCH_OPD 无监视故障 |
| 阀厅地刀通用 |  |
| Q21/Q22/Q23/Q24 OFF | 阀厅紧急门关闭阀厅主门门锁钥匙受限接地刀闸合位无监视故障 |
| Q21/Q22/Q23/Q24 ON | 换流变隔离刀闸分位接地刀闸分位无监视故障 |